# Transformer Losses & Efficiency | Condition for Maximum Efficiency | Solved Numerical | BEEE

Basic Electrical and Electronics Engineering  |  Unit 2: Transformers and electrical machines  |  Presenter: Prof. Mitesh Astik

Topic: Transformer Losses and Efficiency   |   Target length: 8:20 (1166 narrated words at 140 wpm)   |   Audience: engineering undergraduates

## Voice and production notes

Narrator: Prof. Mitesh Astik (male, Indian English, warm and encouraging classroom tone).

Pace: about 140 words per minute. Pause ~1 second after each formula appears on screen.

TTS / voice-clone setting if not recording live: en-IN male neural voice, speed 0.95-1.0.

Say symbols aloud as written in the script (e.g. 's squared', 'zeta', 'omega n'). Say 'ohm', 'newton' naturally.

Visual style: dark-green or white whiteboard look, hand-drawn marker lines, one colour per quantity (force/voltage = red, mass/inductance = blue, damper/resistor = orange, spring/capacitor = green).

## Narrated script  (Timestamp + Scene/Visual  |  Narration)

| Timestamp + Scene / Visual | Narration (word for word) |
| --- | --- |
| 0:00 – 0:18 HOOK Visual: A large power transformer glowing with heat in its core and windings, and an efficiency meter. On-screen text: Where do the losses go? Animation: Animate heat flowing from the core (blue) and windings (orange) of a large transformer; an efficiency meter shows the percentage. AI image/animation prompt: Large power transformer with heat glowing from core in blue and windings in orange and an efficiency meter, flat illustration, 16:9 | A transformer is one of the most efficient machines ever made, often above ninety-eight percent. But for a huge power transformer, even a two percent loss means megawatts of heat. So where do the losses come from, and how do we minimise them? [43 words ≈ 18 sec] |
| 0:18 – 0:38 LEARNING OBJECTIVES Visual: Professor's name card, then a four-item checklist builds on the whiteboard. On-screen text: Prof. Mitesh Astik ¦ Basic Electrical and Electronics Engineering ¦ Unit 2: Transformers and electrical machines By the end you can: 1. List the losses 2. Calculate efficiency 3. Condition for max η 4. Solve a numerical Animation: Tick marks draw themselves beside each objective as it is spoken. AI image/animation prompt: Clean whiteboard with a hand-drawn four-item checklist, friendly male Indian professor avatar in the corner, flat illustration, 16:9 | Namaste, I am Professor Mitesh Astik, and welcome to Basic Electrical and Electronics Engineering. By the end of this video, you will be able to list the losses in a transformer, calculate efficiency, derive the condition for maximum efficiency, and solve a numerical. Let us begin. [46 words ≈ 20 sec] |
| 0:38 – 1:55 SCENE 1: IRON LOSS AND COPPER LOSS Visual: Two panels: core with hysteresis loop and eddy currents; windings with I²R heating. On-screen text: Iron (core) loss Pi = hysteresis + eddy current Hysteresis ∝ f·Bm^1.6 ; Eddy ∝ f²·Bm²·t² Depends on V and f, NOT on load → constant Copper loss Pcu = I1²R1 + I2²R2 = I²·R_eq Depends on load current → varies as (load)² Stray losses: small Animation: On the left, draw the B-H loop with the area shaded as hysteresis loss, and circulating eddy currents on a solid core vs a laminated core. On the right, show current heating the winding. A bar chart shows Pi flat and Pcu growing with load. AI image/animation prompt: Transformer core with hysteresis loop area shaded and eddy currents in laminations, windings with copper loss heat, bar chart of constant iron loss and load dependent copper loss, 16:9 | There are two main losses in a transformer. The iron loss, or core loss, has two parts. Hysteresis loss is due to the repeated magnetisation and demagnetisation of the core, proportional to the area of the B-H loop. Eddy-current loss comes from circulating currents induced in the core, which we reduce with thin laminations. Both depend on the supply voltage and frequency, but not on the load. So the iron loss is constant from no load to full load. The copper loss is the I squared R heat in the windings. It depends on the load current, and varies with the square of the load. At half the load current, the copper loss is a quarter. There are also small stray losses in the tank and in the structure, which we usually ignore. Since a transformer has no moving parts, it has no friction or windage loss, which explains its high efficiency. A quick check on the iron loss: if you double the frequency at constant flux density, the hysteresis loss doubles, and the eddy loss goes up four times. [180 words ≈ 77 sec] |
| 1:55 – 2:43 SCENE 2: EFFICIENCY Visual: Efficiency formula with output, input and loss; fractional load x. On-screen text: η = Output / Input = Output / (Output + Pi + Pcu) At fraction x of full load (same pf): η = x·S·cosφ / (x·S·cosφ + Pi + x²·Pcu,fl) S = rated kVA ; Pcu,fl = full-load copper loss Open-circuit test gives Pi ; short-circuit test gives Pcu Animation: Write the general formula first, then substitute x for fractional load, with arrows showing x multiplying the output and x squared multiplying the copper loss. AI image/animation prompt: Efficiency formula with fractional load x highlighted, x multiplying the output and x squared multiplying copper loss, whiteboard style, 16:9 | Efficiency is the ratio of the output power to the input power. The input equals the output plus the losses. So efficiency equals output divided by output plus iron loss plus copper loss. If the transformer is operated at a fraction x of the full load, with the same power factor, the output becomes x times S times cosine phi. The iron loss does not change, but the copper loss becomes x squared times the full-load copper loss. In practice, the iron loss is found from the open-circuit test, and the full-load copper loss from the short-circuit test. Then we can compute the efficiency at any load, without actually loading the transformer. [112 words ≈ 48 sec] |
| 2:43 – 3:39 SCENE 3: CONDITION FOR MAXIMUM EFFICIENCY Visual: Efficiency vs load curve peaking where the two loss curves cross. On-screen text: η is max when d(losses/output)/dx = 0 Pi / x + x·Pcu,fl is minimum when Pi = x²·Pcu,fl → Iron loss = Copper loss x = √(Pi / Pcu,fl) Load at max η = x × rated kVA Animation: Plot iron loss (flat) and copper loss (parabola) and mark their crossing. Beneath, plot the efficiency curve peaking at the same load. Write the condition and the load fraction formula. AI image/animation prompt: Plot of constant iron loss and parabolic copper loss crossing at one load, and an efficiency curve peaking at the same load, whiteboard style, 16:9 | At what load is the efficiency highest? Divide the numerator and denominator by x S cos phi: efficiency is output over output plus losses, so it is maximum when the loss per unit output, P i by x plus x P cu, is minimum. Differentiate with respect to x and equate to zero. We get P i equal to x squared times P cu. That is, the efficiency is maximum when the iron loss equals the copper loss. The load fraction at maximum efficiency is x equal to root of P i by P cu at full load. Transformers in distribution networks run at partial load most of the time, so they are designed with a low iron loss, to give maximum efficiency at 50 to 70 percent load. [129 words ≈ 55 sec] |
| 3:39 – 5:03 SOLVED NUMERICAL Visual: 25 kVA transformer: iron loss Pi = 350 W, full-load copper loss Pcu = 550 W. Find η at full load and half load (pf 0.8), the load for max η and the max η. On-screen text: Full load, pf 0.8: Output = 25000 × 0.8 = 20000 W ; losses = 350 + 550 = 900 W η = 20000/20900 = 95.69 % Half load (x = 0.5): Output = 10000 W ; Pcu = 0.25 × 550 = 137.5 W ; losses = 487.5 W η = 10000/10487.5 = 95.35 % Max η: x = √(350/550) = 0.798 → load = 19.94 kVA ; Output = 0.798 × 20000 = 15954 W ; losses = 2 × 350 = 700 W η_max = 15954/16654 = 95.80 % Animation: Show the three load conditions as three rows of a table filling in output, losses and efficiency. Plot the three points on the efficiency curve, with the peak highlighted. AI image/animation prompt: Table of output losses and efficiency for full load half load and maximum efficiency load, and the efficiency curve with these points marked, whiteboard style, 16:9 | Let us solve one. A 25 kilovolt-ampere transformer has an iron loss of 350 watts, and a full-load copper loss of 550 watts. Find the efficiency at full load and at half load, both at 0.8 power factor, and the load at which the efficiency is maximum. Full load. Output equals 25,000 into 0.8, equals 20,000 watts. Total loss equals 350 plus 550, equals 900 watts. Efficiency equals 20,000 by 20,900, equals 95.69 percent. Half load. Output equals 10,000 watts. The copper loss becomes one-quarter of 550, which is 137.5 watts. Total loss equals 350 plus 137.5, equals 487.5 watts. Efficiency equals 10,000 divided by 10,487.5, equals 95.35 percent. Maximum efficiency. The load fraction x equals root of 350 by 550, equals 0.798. The load is 0.798 into 25, equals 19.94 kilovolt-ampere. At this load, the copper loss equals the iron loss, 350 watts, and the total loss is 700 watts. The output is 0.798 into 20,000, equals 15,954 watts. Efficiency equals 15,954 by 16,654, equals 95.80 percent. Notice how flat the curve is: 95.35 at half load, 95.80 at the best, 95.69 at full load. A transformer keeps a high efficiency over a wide range of loads. [198 words ≈ 85 sec] |
| 5:03 – 6:59 COMMON MISTAKES AND EXAM TIPS Visual: Efficiency mistakes. On-screen text: 1. Output uses power factor: kVA × pf 2. Iron loss does not change with load 3. Copper loss scales with x² 4. Max η load depends on √(Pi/Pcu) Animation: Each tip appears as a red 'WRONG' note that flips to a green 'RIGHT' note with a marker tick. AI image/animation prompt: Whiteboard with red crossed-out wrong working and green corrected working side by side, exam-tips banner, flat style, 16:9 | Four points. One: the output in watts is kilovolt-ampere times the power factor. Do not forget the power factor. Two: the iron loss does not change with the load. Three: the copper loss changes with x squared, not x. Four: the maximum efficiency does not occur at full load unless the iron loss equals the full-load copper loss. And note, the maximum efficiency is different for different power factors, because it changes the output. But the load fraction at which it occurs is the same. In a real power plant, transformers are chosen so that their maximum efficiency matches the typical load. Over a year, that saves a great deal of energy. How do we actually find the two losses in a laboratory? Without loading the transformer, using two tests. In the open-circuit test, the rated voltage is applied to the low-voltage winding, with the high-voltage winding open. The current is very small, so the copper loss is negligible, and the input power equals the iron loss. In the short-circuit test, the high-voltage winding is supplied with a reduced voltage, only a few percent of the rated value, until the rated current flows, with the low-voltage winding shorted. The flux is then very low, so the iron loss is negligible, and the input power equals the full-load copper loss. These two tests are economical: they need only a small amount of power, yet give the full-load efficiency. For distribution transformers that are loaded lightly most of the day, designers also look at the all-day efficiency, which is the ratio of the energy output to the energy input over 24 hours. [270 words ≈ 116 sec] |
| 6:59 – 7:34 RECAP Visual: Five bullets appear with tick marks over a faded replay of the main diagram. On-screen text: 1. Iron loss: constant (hysteresis + eddy) 2. Copper loss ∝ (load)² 3. η = xScosφ / (xScosφ + Pi + x²Pcu) 4. Max η when Pi = x²Pcu 5. x = √(Pi/Pcu) at max η Animation: Each bullet types in with a green tick; the main diagram pulses once at the end. AI image/animation prompt: Five-point recap slide on a whiteboard with green ticks and small icons, faded main diagram in the background, flat style, 16:9 | Let us recap in five points. One: iron loss is constant and comes from hysteresis and eddy currents Two: copper loss varies as the square of the load Three: efficiency at fraction x of load is x S cos phi over x S cos phi plus P i plus x squared P cu Four: efficiency is maximum when iron loss equals copper loss Five: the load fraction at maximum efficiency is the root of iron loss by full load copper loss [81 words ≈ 35 sec] |
| 7:34 – 8:20 CLOSING: PRACTICE + NEXT VIDEO Visual: Two practice questions on screen; then a teaser animation for the next topic. On-screen text: Practice 1: 10 kVA transformer, Pi = 150 W, Pcu(full load) = 250 W. Find η at full load, unity pf. Practice 2: For the same transformer, find the load fraction at maximum efficiency. Next: DC Motor: Principle, Back EMF and Torque Equation Animation: Questions slide in one by one with a 'Pause the video' icon. Teaser animation plays, then the Subscribe bell animation in the corner. AI image/animation prompt: A DC motor armature turning in a magnetic field with current and force arrows, with a Subscribe button and a Pause icon, 16:9 | Now it is your turn. Pause the video and try two questions. Question one: a 10 kilovolt-ampere transformer has an iron loss of 150 watts and a full load copper loss of 250 watts. Find the efficiency at full load and unity power factor. Question two: for the same transformer, find the load fraction at maximum efficiency. Answers are in the pinned comment. In the next video, we move on to the DC motor: how it works, the back emf and its significance, and the torque equation. If this helped, like, subscribe, and share it with your classmates. Thank you, and see you in the next lecture. [107 words ≈ 46 sec] |

## Instructor answer key (do not show on screen)

Practice 1 answer: η = 10000/(10000 + 400) = 96.15 %.

Practice 2 answer: x = √(150/250) = 0.775 (77.5 % of full load).

# YouTube package

### Video title

Transformer Losses & Efficiency | Condition for Maximum Efficiency | Solved Numerical | BEEE

### Description with chapters

Prof. Mitesh Astik explains the iron and copper losses in a transformer, the efficiency formula, the condition for maximum efficiency, and a worked numerical with the efficiency at different loads.

Chapters:

0:00 Hook

0:18 Learning objectives

0:38 Iron Loss And Copper Loss

1:55 Efficiency

2:43 Condition For Maximum Efficiency

3:39 Solved Numerical

5:03 Common Mistakes And Exam Tips

6:59 Recap

7:34 Closing: Practice + Next Video

Subscribe for the full series covering every unit of the syllabus. Practice-question answers are in the pinned comment.

### 10 tags

transformer efficiency, iron loss copper loss, maximum efficiency condition, transformer losses, hysteresis loss eddy current loss, transformer numerical, basic electrical engineering, BEEE, Prof Mitesh Astik

### Thumbnail text idea

TRANSFORMER EFFICIENCY  |  Pi = Pcu  |  Maximum η = 95.8%

Layout: presenter cut-out on the right, big bold text on the left (yellow on dark), the key diagram (circuit / spring-damper) glowing in the centre.

# Series roadmap (syllabus coverage)

| Syllabus unit | Suggested episodes |
| --- | --- |
| Unit 1 | Ep1. Mesh and nodal analysis of DC circuits Ep2. AC fundamentals: average value, RMS value, form factor and peak factor Ep3. Phasor representation of alternating quantities Ep4. Series R, L, C, RL, RC and RLC circuits Ep5. Real, reactive and apparent power and power factor Ep6. Power and energy in DC circuits and maximum power transfer |
| Unit 2 | Ep7. Single-phase transformer: principle, construction and EMF equation Ep8. Transformer losses and efficiency <-- THIS VIDEO Ep9. DC motor: principle, back emf and torque equation Ep10. DC shunt motor characteristics and speed control Ep11. Three-phase induction motor |
| Unit 3 | Ep12. Semiconductor diode and equivalent circuits Ep13. Half-wave and full-wave bridge rectifiers Ep14. Zener diode as voltage regulator |
| Unit 4 | Ep15. BJT construction, operation and BJT as a switch Ep16. n-channel enhancement MOSFET Ep17. Common-source amplifier, DC load line and MOS inverter |
| Unit 5 | Ep18. Op-amp introduction, specifications and differential/common-mode operation Ep19. Inverting, non-inverting and summing amplifiers Ep20. Integrator, differentiator and comparator Ep21. 555 timer astable mode and 78XX voltage regulators |